DETAIL: SLWG-04 DATE: 03/2020 SCALE: N.T.S.
SHEET: 1 OF 1

MINIMUM CONSTRUCTION STANDARDS FOR ST. LUCIE WEST SERVICES DISTRICT
450 SW UTILITY DRIVE, PORT SAINT LUCIE, FL 34986 PHONE: (772) 340-0220

STANDARD SEPARATION REQUIREMENTS

MINIMUM SEPARATION BETWEEN SLWSD FACILITIES AND OTHER UTILITIES

OTHER PIPE	HORIZONTAL SEPARATION	CROSSINGS (1)	JOINT SPACING @ CROSSINGS (FULL JOINT CENTERED)	

GRAVITY OR
PRESSURE SANITARY SEWER, SANITARY SEWER FORCE MAIN, RECLAIMED WATER (3),
VACUUM SANITARY SERVICE	
WATER MAIN 10' MINIMUM	
WATER MAIN 18' MINIMUM	

6' MINIMUM

WATER MAIN	
				
	(4)			
ALL OTHER FACILITIES, INCLUDING BUT NOT LIMITED TO:
STORM SEWER, STORMWATER FORCE MAIN,
RECLAIMED WATER (2),	SLWSD FACILITY

5' MINIMUM	SLWSD FACILITY
(4)
18' MINIMUM	

3' MINIMUM	
TELEPHONE, CABLE TV, POWER, ETC.			WATER MAIN	
				
ON-SITE SEWAGE TREATMENT AND DISPOSAL SYSTEM	10' MINIMUM	- - - - -	- - - - -